|  | Approved by:. Technical Director of "TERMOELECTRICA" S.A.. ” ”; ” ”; 20. |
| --- | --- |

TENDER BOOK

No._____ of ”___”  ”____________” 20___ , batch no. _____

for acquisition of  material goods

Object of the tender book

Procurement of fire heating oil.

| No. | Code CPV | Name of the good | U.M. | Quantity | Estimated value, without VAT MDL |
| --- | --- | --- | --- | --- | --- |
|  | 09135100-5 | Heating oil (brand M100 or its equivalent) | tons | 20.000 | 333 333 334 |

- General description. Terms of execution

  - Place of delivery: 3, Master Manole str., mun. Chisinau, Republic of Moldova,  – CET Source 1. (Fuel Service – Heating Oil Management unit).

  - Deadline for completion of the procurement: the delivery will be made in the period October-November.

- Purpose of the procurement

Procurement of fire heating oil for the purpose of stocks replenishing.

- Basic Parameters

Physico-chemical characteristics:

- Viscosity at a temperature of  +80 0C:

Conventional (technical) viscosity, 0E –                                    8 -  16.0;

Kinematic viscosity, m2/sec –                           			59 * 10-6 – 118 * 10-6;

Centistockes (cSt) –                                                                    59 - 118;

2.	Ash content, in %, not more than –                                  	0.14;

3.	The content of mechanical impurities, in %, not more than –  1.0;

4.	Water content, in %, not more than –                           	    1.0;

5.	Sulphur content, in %, not more than –                                    1.0;

6. Explosion temperature, in 0C, in open shuttle, not less than –   110;

7.	Solidification temperature, in 0C, not higher than –                  25;

- 8. Energy released at combustion (minimal), in kJ/kg, not less than – 40530.

  - The tenderer shall submit the certificate confirming the compliance of the good with the requested basic parameters

- Used materials, compatibility, technical regulations and standards

– The fire heating oil must meet the requirements of GOST 10585-99 "Топливо нефтяное. Мазут. Технические условия "or the equivalent of the European standard.

– To comply with the requirements of the Regulation "on reduction of the sulphur content of certain liquid fuels" approved by the Government Decision no.414 of 8 April 2016.

- Law no. 461 of 30.07.2001 on the market of petroleum products, Article 18. Import of petroleum products, Article 22. Transportation of petroleum products.

- General Conditions of Tender

5.1. The technical proposal shall contain:

- Certificates of origin/provenance and conformity/quality

- Proof of experience in the field of oil production;

- Detailed description of the delivery method/route;

5.2. Heating oil acceptance conditions:

-	The entry control of the good is performed at the time of stationing of the train with heating oil at the Buyer's warehouse, by the Buyer in accordance with РД 34.09.105-96 ”МЕТОДИЧЕСКИЕ УКАЗАНИЯ ПО ОРГАНИЗАЦИИ УЧЕТА ТОПЛИВА НА ТЕПЛОВЕХЛЕЛЛЛЕКЛЕКТРОСТАНЛИЯ”. In order to comply with the accuracy of measuring the quantity of fuel oil, the transportation shall be carried out only by rail with calibrated railway tanks.

- In case of compliance with the requirements of the technical criteria stipulated in Chapter 5, the quantity and quality of the product, as well as the presentation of the entire set of documents, the act of receipt of the good is signed and the reception of the good is fulfilled at the Buyer's warehouse .

- In case of finding the inadequate quality of the request, by the Buyer, the Seller removes the non-conformity by changing the non-conforming good (the entire party) within 30 calendar days;

- All expenses for logistics, transportation, taxes, customs duties, weighing of tanks and other costs are borne by the Seller, in accordance with the transportation contract concluded between the Seller and the State Enterprise "Railway Station of Moldova".

- The delivery will be made at the seller's expense and with the Seller's means of transport to the Buyer's warehouse, 3, Master Manole str., mun. Chisinau, Republic of Moldova, (Heating oil management unit, CET Source 1), maximum 24 tank wagons per daily allowance, which shall be accompanied by the Analysis Report and Quantity Report issued by an accredited body according to ISO 17025, until the total delivery of the requested quantity.

- Contact : Tel.: 022-385-391;    e-mail: spinu.alexandr@termoelectrica.md

Tel.: 022-436-490 ;    e-mail: vlaico.mariana@termoelectrica.md;

| Drafted by: | Head of SCb |  | Alexandr Spînu |  |
| --- | --- | --- | --- | --- |
| Approved: |
|  | Deputy Technical Director (Production) |  | Lilian Munteanu |  |
|  | Head of SMT |  | Carolina Cebotari |  |
|  | Head of SPOM |  | Bugaian Tatiana |  |

str. 31 August, 129, Chişinău, Moldova Tel./fax (+ 373.22) 233997, 234401 intertext.md

| Subsemnata, Barcaru Lilian, traducător (limba engleză), certific exactitatea traducerii cu textul înscrisului, care a fost vizat de mine la 18.08.2022. | I, the undersigned, Barcaru Lilian, translator (English), certify the accuracy of the translation which corresponds to the text, which was signed by me on 18.08.2022. |
| --- | --- |

Semnătura traducătorului

Translator’s signature